## BOQ
Bill of Quantity
Name of work :- Supply, installation, testing commissioning of Air handling Unit of 8000 CFM x 2 Nos capacity at Lecture Hall (L-5 & 6) with associated works.
Name of Agency
S.No. | DISCRIPTION | QTY. | Unit | RATE Rs. | AMOUNT Rs.
EQUIPMENT & PIPING
DOUBLE SKIN AIR HANDLING UNITS
AIR HANDLERS UNITS
1 | Supply, Installation, Testing and Commissioning of double skin sheet metal construction horizontal floor mounted air handling units with 50 mm thick injected PUF of density not less than 40Kg/CuM.The air handling units shall be complete with synthetic fibre filters (EU-4) , coil section with multirows deep chilled water cooling coil of copper tube and aluminium fins construction, fan section complete with backward curved DIDW centrifugal fan , belt drive package, VFD compatible variable speed squirrel cage induction motor (IE-3), stainless steel drain pan , manually operated supply air damper (AL) and vibration isolation pads all complete as per specifications.AHUs shall be selected for a maximum face velocity of 500 FPM (2.5 MPS)and as per schedule of air handling units under appendix VIII. Fan outlet velocity shall not exceed 1800 FPM (9.1 MPS).
a) | 8000 CFM, 6Rows, static pressure 60 mmwg, | 2 | Nos. |  | 0
2 | Supply, Installation,Testing and Commissioning of variable frequency drives for following Air Handling Units.Variable frequency drives shall be provided with necessary temperature sensors and transmitters complete with control wiring in all respect as required and as per specs. The drives shall be suitable for the following motor rating. VFDs shall be housed in the AHU electrical Panels.
a) | 3.7- 4.0 KW (FC-102 Series) danfoss or equivalent. | 2 | Nos. |  | 0
3 | Supplying & laying , testing & commissioning mild steel ' C ' class pipe of size as mentioned below on exposed surface / underground with fabrication of bends, tees, reducers, ( brick masonry block & wooden support for underground / MS angle- clamp & wooden support for exposed surface ) alongwith priming coat of steel primer as per standard specification
a) | 100 mm | 5 | Mtr |  | 0
b) | 80 mm | 5 | Mtr |  | 0
c) | 65 mm | 15 | Mtr |  | 0
d) | 50 mm | 10 | Mtr |  | 0
e) | 32 mm | 3 | Mtr |  | 0
f) | 25 mm | 5 | Mtr |  | 0
4 | Supplying & fixing, insulation on existing pipe on exposed surface / underground of following sizes with 50 mm thick thermocole ( polystrene) pipe section alongwith hessian cloth, wiremesh, bitumen, & cement - sand plaster, painting two or more coat to give even shade after applying one coat of ordinary paint etc complete as required.
a) | 100 mm | 5 | Mtr |  | 0
b) | 80 mm | 5 | Mtr |  | 0
c) | 65 mm | 15 | Mtr |  | 0
d) | 50 mm | 10 | Mtr |  | 0
e) | 32 mm | 3 | Mtr |  | 0
f) | 25 mm | 5 | Mtr |  | 0
5 | Supplying, laying/ fixing, testing and commissioning of G.I 'B' class pipe with 19 mm nitrile insulation of following sizes for drain water piping on surface / underground (including fabrication of bends, tees, reducers) with suppport and fittings as per standard specification complete as required.
a) | 50 mm | 10 | Mtr |  | 0
b) | 32 mm | 10 | Mtr |  | 0
6 | SITC of butterfly valves CI body with SS Disc Nitrile Rubber Seal & O- Ring PN 16 pressure rating for chilled water with hand lever operated including nut, bolt, flanges, gasket as kind of existing pipe, painting with enamel etc. complete as reqd.
a) | 65 mm | 2 | No. |  | 0
b) | 50 mm | 2 | No. |  | 0
7 | Y - STRAINER of Ductile CI Body flanged ends with stainless steel strainer forchilled / hot water circulation as specified.
a) | 65 mm | 1 | No. |  | 0
b) | 50 mm | 1 | No. |  | 0
8 | Supply and fixing of ss ball valve of following size with socket and nipple of approved make or equivalent complete as required.
a) | 25 mm | 4 | Nos. |  | 0
9 | Supply and fixing industrial type thermometer of proportioning length with adjustable angle, direct reading including thermowell socket. Thermometer shall be suitable to read water temperature of range 0°C to 50°C completed as required. | 4 | Nos |  | 0
10 | Providing and fixing 0-150 PSIG industrial type pressure gauge in position of 65/100 mm dia with petcock valves (gun metal / brass) complete with pressure snobber, nipple etc complete as required. | 4 | Nos |  | 0
11 | Cutting, dismantling and removing old damaged/defective insulation of thermocole insulation (i.e.- hessian cloth, wire mesh, send, cement, plaster) from chilled water pipe line of following size, cleaning of pipe and shifting the waste material up to desired location as reqd.
a) | 20 mm to 100 mm dia | 5 | Mtr |  | 0
12 | Cutting and dismantling of damaged/defective MS pipe of following size (on surface/recessed/underground ) i/c shifting to sectional store complete as required.
a) | 20 mm to 100 mm dia | 5 | Mtr |  | 0
AIR DISTRUBUTION & INSULATION
13 | Supplying, fabricating, installing and testing of GI sheet metal fabricated ducts complete with supports Vanes, dampers. Links levers and quadrants etc. as per specification and drawings. The flanges shall be of hot dip galvanized. The rates shall include.
a) | 22 gauge | 40 | sqm |  | 0
b) | 24 Gauge | 100 | sqm |  | 0
14 | Supplying and fixing of following thickness duly laminated aluminum foil of mat finish closed cell Nitrile rubber (Class “O”) insulation on existing duct after applying suitable adhesive for Nitrile rubber. The joints shall be sealed with 50 mm wide and 3 mm thick self adhesive nitrile rubber tape insulation complete as per specifications and as required.
a) | 19 mm thick | 150 | SqM |  | 0
15 | Providing & fixing of accoustic insulation with open cell nitral rubber supersilence (self adhesive) for AHU room of following thickness, on existing surface with Adhesive/ dentrite etc. complete as required. (As per specification)
a) | 25 mm thick | 40 | SqM |  | 0
b) | 15 mm thick | 40 | SqM |  | 0
16 | Supply & Application of acoustic lining/ internal thermal insulation of supply/return air ducting with fibre glass insulation as per the specifications and drawings.
a) | 25 mm thick | 24 | sqm |  | 0
17 | Supply, Installation , Testing and Commissioning of smoke cum fire dampers of at least 90-120 minutes fire rating as per the approved shop drawings and specifications. Interlocking of fire dampers using copper control wiring shall be affected as required.
a) | Bare fire dampers | 1.2 | SqM |  | 0
18 | Supply, Installation, Testing & Commissioning of smoke cum fire dampers of at least 90 minutes fire rating as per the approved shop drawings and specifications. Interlocking of fire dampers using copper control wiring shall be affected as required.
a) | Actuator with control panel, temperature sensor & spring return action and suitable for 10-12 NM Torque. | 2 | No. |  | 0
19 | Supply, installation, testing and commissioning of powder coated Aluminium extruded liner multislot type HIT & MIS Diffusser with damper as specification & the sizes will be as per schedules and drawing. | 2 | Sqm |  | 0
20 | Supply, fixing, testing & commissioning of supply air diffusers suitable for fixing Grid/Gypsum ceiling of power coated aluminium with aluminium control dampers with anti smudge ring & removable core. | 2 | sqm |  | 0
21 | Supplying, fixing, testing commissioning of return air diffusers of powder coated aluminium without volume control dampers with anti smudge ring & removable core… | 2 | sqm |  | 0
22 | Dismantling and removing of existing old ducts of any size i/c removing of hangers, flanges, valve etc. as reqd. | 40 | SQM |  | 0
23 | Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc., as per specifications. | 1 | SqM |  | 0
24 | Supply,Installation, Testing and Balancing of spigots factory fabricated out of galvanised steel sheet of different sizes to facilitate flexible duct connection.
a. | 200mm dia | 4 | No. |  | 0
25 | Supply, Installation, Testing and Commissioning of pre-insulated factory fabricated flexible ducts inner as well as outer skin constructed out of reinforced aluminium foil as per the specifications. Ducts shall be of following sizes :
a. | 200mm dia | 4 | RM |  | 0
26 | Supply, installation, testing and commissioning of factory fabricated LP Plenum for Multislot diffuser for supply air duly fitted on G.I Frame with nut, bolt and washer between diffuser and flexible duct etc, complete as required.
a) | 800 X 250 X 250 mm | 4 | Nos. |  | 0
POWER & CONTROL WIRING
27 | S & Laying of one no. PVC insulated copper conductor un-armoured control cable of 1.1 kV grade of following size and core.
a) | 4 x 6 sqmm (on surface) | 15 | Mtr |  | 0
28 | Supplying and laying 6 SWG G.I. wire at 0.50 metre below ground level for conductor earth electrode, including connection/ termination with GI thimble etc. as required. | 15 | Mtr |  | 0
29 | Supply, installation, testing & commissoning of wall mounted cubicle type electrical panels including system control wiring with incoming, outgoing feeders as described below and as per specifications. AHU panel casing shall be large enough to accommodate variable frequency drives. VFDs have been accounted for seperately under equipment portion schedule of quantities.
Panel-A (VFD PANEL)
Location : AHU Room
a | 16 A TP MCB for 3.7-4.0 Kw motor -01 set.
b | Digital type voltmeter (0-500) V, digital type Ammeter, selector switches, RYB LED type indication lights --01 set.
c | Auto-manual type selector switch to facilitate auto start of AHU after toration of power.
d | Control wiring & safety circuit as required with start-stop PB's stayput or lockable type and tow sets of LED type ON OFF indication lights AHU panel as described above. | 2 | No. |  | 0
CIVIL ITEMS
30 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge.
a) | In cement mortar | 4 | Cum |  | 0
31 | Providing and fixing double scaffolding system (cup lock type) on the exterior side, up to seven story height made with 40 mm dia M.S. tube 1.5 m centre to centre, horizontal & vertical tubes joining with cup & lock system with M.S. tubes, M.S. tube challies, M.S. clamps and M.S. staircase system in the scaffolding for working platform etc. and maintaining it in a serviceable condition for the required duration as approved and removing it there after .The scaffolding system shall be stiffened with bracings, runners, connection with the building etc wherever required for inspection of work at required locations with essential safety features for the workmen etc. complete as per directions and approval of Engineer-in-charge .The elevational area of the scaffolding shall be measured for payment purpose .The payment will be made once irrespective of duration of scaffolding. Note: - This item to be used for maintenance work judicially, necessary deduction for scaffolding in the existing item to be done. | 200 | SqM |  | 0
| Sub Total |  |  |  | 0
32 | Buy Back Cost of Old AHU including dismantling removing and taken away from side (except motor).3 phase Electric Motor will be shifted to the sectional store by the contractor. | 2 | No. |  | 0
| Total |  |  |  | 0
Notes:- The above work may also have to be executed during night shift from 6:00 PM to 6:00 AM in addition to normal working hours in case of requirement during running of classes (if required).