## boq
BILL OF QUANTITY
Sub: | Maintenance of SHW System i/c replacement of old damaged SS Tanks, GI pipe, insulation, cladding, valve etc and associated works at Hall-4 Mess & E-1 block.
Name of Agency :-
S.No. | Description | Qty | Unit | Rate | Amount
1 | SITC of min 3.0 mm thick Horizontal Cylindrical SS storage tank as approved per drawing of following capacity with both end plates made by Argon Tig welding method of SS-304 grade stainless steel sheet and SS-304 fittings i.e. 20 mm SS socket @ 2 no's for Air-vent & Drainage , 25 mm SS socket @ 4 no's for piping work, 32/38 mm SS socket @ 2 no's for heating element and 9.52/12.7 mm SS socket @ 1 no for thermostat. Tank should be factory and site tested on min 2 Kg/Sq.cm for water leakage for SHW storage system complete as required. (Note:-Lifting/Shfting, SS Patches also work includes for SS fittings).
a) | 1000 Ltr. capacity | 2 | Nos. |  | 0
2 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end). |  |  |  | 0
a) | 20 mm. | 2 | Nos. |  | 0
b) | 25 mm. | 12 | Nos. |  | 0
3 | S/ Replacement of following size 304 grade SS threaded nipple following size i/c dismantling old if any complete as required. |  |  |  | 0
a) | 3/4"x6" | 1 | Nos. |  | 0
b) | 1"x6" | 8 | Nos. |  | 0
c) | 1.25"x6" | 1 | Nos. |  | 0
4 | S/ Replacement of 25 mm SS flanged-nipple of SS- 304 grade having approx. 65 mm flange with welded 4"/6" nipple with 4 Nos. S S nut, bolt, washer & EPDM gasket i/c dismantling old if any complete as required. |  |  |  | 0
a) | 1"x6" | 6 | Nos. |  | 0
5 | P & F of following size 304 grade SS socket with welding and refilling etc and making water leakage proof i/c dismentalling old if any complete as reqd. |  |  |  | 0
a) | 1"x6" | 2 | Nos. |  | 0
b) | 1.25"x6" | 1 | Nos. |  | 0
6 | S/ Replacement of dead flange 5 mm thick of 304 grade SS having approx. 65mm outer dia with 4 Nos.S S nut, bolt & washer i/c dismentalling old if any complete as required. | 6 | Nos. |  | 0
7 | Providing and fixing G.I. "B" Class pipes complete with G.I. fittings and clamps, i/c cutting and making good the walls etc.Internal work - Exposed on wall. |  |  |  | 0
a) | 25 mm. | 25 | Mtrs. |  | 0
b) | 20 mm. | 7 | Mtrs. |  | 0
8 | Dismantling and refixing of pipe line upto 25mm by providing and fixing required fittings etc complete as required | 60 | Mtrs. |  | 0
9 | Dismentling of the old pipe line of the system and depositing same in the sectional store i/c cartage complete as required. | 25 | Mtrs. |  | 0
10 | S/Replacement of defective and damaged insulation on following size pipe line for hot water pipe line with 50 mm thick LRB Mattress Standard IS-3144, having Min 100kg/Cu-m density with 24 g chicken wire mesh etc complete as required . |  |  |  | 0
a) | 25 mm. | 45 | Mtrs. |  | 0
b) | 20 mm. | 7 | Mtrs. |  | 0
11 | S/Replacement of defective and damaged insulation on SHW SS tank with 50 mm thick LRB Mattress Standard IS-3144, having Min 100kg/Cu-m density with 24g chicken wire mesh etc complete as required. | 18 | SqM. |  | 0
12 | S/Replacement of defective and damaged aluminium cladding with 26 swg thick aluminium sheet on outer surface for 25 mm/ 20 mm G.I pipe having 50 mm thick insulation i/c fixing with screws complete as required (Make-Hindalco/Equiv.)
a) | 25 mm. | 45 | Mtrs. |  | 0
b) | 20 mm. | 7 | Mtrs. |  | 0
13 | S/Replacement of defective and damaged Aluminium clading with 26 swg thick aluminium sheet i/c fixing with screws complete as required (Make-Hindalco/Equv). | 18 | SqM. |  | 0
14 | Supply and making aluminium cladding bend appx. 500 mm circumference outer suitable for following size G.I pipe with insulation. i/c fixing with screws complete as required. (Make-Hindalco/Equiv.)
a) | 25 mm. | 12 | Nos. |  | 0
15 | S/Replacement of 3.0 Kw industrial type water imersion heating element ( ISI marked) with pocket and 7" rod thermostat along with connecting wire, complete as reqd. | 6 | Nos. |  | 0
16 | Dismantling, cleaning, discaling, overhauling of Solar hot water panel (100 lPD) of installed SHW system with proper descaling chemical etc and reassembling, testing, commissioning i/c. P/F all ss nut, bolt, epdm gasket & ss washers etc as reqd. | 28 | Nos. |  | 0
17 | Locating and repairing leakage of Solar hot water panel (100 lPD) i/c dismantling of damage copper tubes, Upper & lower header, drilling and brazing with required sizes tube, flanges etc, making leak proof and painting with black paint and reassembling the panel as reqd. | 5 | Nos. |  | 0
18 | Painting min two coat with super enamel Paint of SHW complete Panel (100 LPD) including panel stand, SS tank stand and makeup tank stands, pipe sports after cleaning the surface with sand paper/ cloth etc as reqd. | 28 | Nos. |  | 0
19 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | 350 | Kgs. |  | 0
20 | Providing & laying GI Flexible conduit of following size for existing Power/controle cabling etc i/c clamp and screwing etc complete as reqd. | 20 | Mtrs. |  | 0
21 | Providing anf fixing of fabricated MS Clamp for flate plate collectors having one side tightning arrangemet with 10 mm welded nut-bolt as reqd. | 16 | Nos. |  | 0
22 | P & F of 32 Amp 2 Pole MCB with 2/4 Way powder coated MS Box enclosure suitable for 3.75 kW i/c dismantling old if any complete as required. | 2 | Nos. |  | 0
23 | Providing and fixing float ball valve (brass) of approved quality, High or low pressure, with plastic floats complete as req.
a) | 25 mm. | 2 | Nos. |  | 0
24 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level. | 1 | CuM |  | 0
25 | Structural steel work welded in built up sections and framed work, i/c cutting, hoisting, fixing and applying a priming coat complete as required.(Labour only) | 40 | Kgs. |  | 0
| Total Rs. |  |  |  | 0