## BoQ1 (hidden)
Item Rate BoQ
BoQ_Ver3.0 | Item Rate | Normal | INR Only | INR
Select, Excess (+), Less (-) |  | Less (-)
Tender Inviting Authority: Superintending Engineer, IWD IIT Kanpur
Name of Work: Construction of vertical extension (i.e. 5th to 8th floor) of National Aerosol Test Facility Building at IIT Kanpur (SH:- Airconditioning Works)
Contract No: 18/AC/2020/1268 dt. 23.12.2020
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevent columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder in Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT Without Taxes in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55
1 | SUBHEAD 1: VARIABLE REFRIGERANT VOLUME | item1 | [52 empty] | 1 | Construction of chamber for 100mm sluices valve | item1 | 10 | 1 Nos
1.01 | VARIABLE REFRIGERANT FLOW SYSTEM | item2 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.02 | Supply, Installation, testing and commisioning of modular type Variable Refrigerant Flow/Variable Refrigerant air cooled Outdoor units suitable for cooling and heating,having all hermetically sealed Inverter Scroll Compressor(s), minimum two compressors for above 14 HP modules, microprocessor based Controller, top discharge type condensing unit (s), with R 410 A Refrigerant, vibration isolators, with suitable foundation and with in built auto phase sequencer etc. complete as required. The unit shall deliver the rated capacity at AHRI Conditions and work even at 50⁰ C ambient temperature without tripping. The unit shall be suitable to work on 415±5%, 3 phase, 50 Hz AC power supply. The unit shall be filled with first charge of the refrigerant and ready for use as required. The COP at AHRI conditions shall not be less than 3.1 and IEER not less than 6.5. | item3 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.03 | Outdoor Units | item4 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.04 | 36 HP ((18HP+18 HP) or (16HP+20 HP)) | item5 | 4 | No. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.05 | 16 HP | item6 | 2 | No. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.06 | INDOOR UNIT DUCTABLE TYPE | item7 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.07 | Supply, installation, testing and commissioning of following minimum capacity and external static pressure VRF/VRV ceiling mounted ductable type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, corded remote control, outer cabinet, vibration isolators, drain pan, other necessary supports etc., suitable for operation on single phase AC supply 230 V ± 10%, 50 Hz or 415 ± 5 %, 3 phase, 50 Hz AC power supply for units aboe 4.6 TR complete as required. The unit shall have automatic force shut down provision in case of fire on receiveing signal from BMS System. The cooling capacity of indoor unit will be at air inlet conditions of 27 Degree C DB and 19 Degree C WB temperature. | item8 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.08 | Medium Static ductable Unit | item9 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.09 | Ductable unit : 3.4 TR, 1200 CFM (nominal) min. 38200 btu/hr | item10 | 4 | No. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.1 | Ductable unit : 4.0 TR, 1600 CFM(nominal), min 47800 Btu/hr | item11 | 12 | No. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.11 | Ductable unit : 4.5 TR, 1960 CFM (nominal), min 54600 Btu/hr | item12 | 4 | No. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.12 | INDOOR UNIT CASSETTE TYPE | item13 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.13 | Supply, installation, testing and commissioning of following minimum capacity 4-way flow VRV/VRF Cassette Type Indoor ceiling mounted unit equipped with synthetic washable media pre-filter, fan section with low noise fan/ dynamically balanced blower, multispeed motor, coil section with DX copper coil, electronic expansion valve, outer cabinet, drain pump, grille, necessary supports, vibration isolation, cordless remote control etc., suitable for operation on single phase 230 ± 10%, 50Hz AC supply, complete,as required. The Unit shall have automatic force shut down provision in case of fire on receiving signal nfrom BMS System. The cooling capacity of indoor unit will be at inlet condition of 27 degree C DB and 19 degree C WB temperature. | item14 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.14 | 4-Way Cassette Unit | item15 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.15 | 4-Way Cassette unit : 1.0 TR or heigher capacity | item16 | 9 | No. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.16 | 4-Way Cassette unit : 1.3 TR or heigher capacity | item17 | 9 | No. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.17 | 4-Way Cassette unit : 1.6 TR or heigher capacity | item18 | 5 | No. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.18 | 4-Way Cassette uni : 2.0 TR or heigher capacity | item19 | 1 | No. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
1.19 | Controllers | item20 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
1.2 | SITC of wall mounted wired/wireless Room Thermostat/Controller as per specification | item21 | 4 | No. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
1.21 | SITC of following type BMS/IMS Digital central controller with touch screen panel of min 10.1 inch size, including hardware and software compatible to VRF/VRV system by Original equipment manufature (OEM) suitable for min 48 no's circuits, 50 no's ODU's & 200 no's IDU's. The system shall provide communication through LAN & Bacnet. The unit operation on single phase AC supply 230V±10%, 50Hz by which following minimum operations are compulsoraly required 1) Electric power consumption and electricity charge distribution of individiual IDU. 2) Fault/Operation display, Operation history reports in USB or PC in suitable format 3) Web access and annual Operation management, complete as per specification. | item22 | 1 | No. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
1.22 | Communication cable(1.5 sqmm X 2 Core) in pvc conduit as per specification | item23 | 550 | Rmt | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
2 | Treated Fresh Air Unit (TFA) | item24 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
2.01 | Supply, installation, testing and commissioning of following minimum capacity and external static pressure VRF/VRV ceiling mounted Treated fresh air (TFA) ductable type Indoor unit equipped with washable synthetic media pre-filter, fan section with low noise fan/dynamically balanced blower, multi speed motor, coil section with DX copper coil, electronic expansion valve, outer cabinet, vibration isolators, drain pan, other necessary supports etc., suitable for operation on single phase AC supply 230V±10%, 50Hz complete as required. The unit shall have automatic force shut down provision in case of fire on receiving signal from BMS System. The cooling capacity of indoor run it will be at air inlet conditions of 33 Degree C DB and 28 Degree C WB temperature. | item25 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
2.02 | TFA Indoor Ductable unit : 6.67 TR (988 cfm) | item26 | 4 | No. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3 | REFRIGERANT PIPING | item27 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3.01 | Supply, fabrication, installation, testing of Interconnecting refrigerant pipe work with XLPE insulation between each set of indoor & outdoor units as per specifications, all piping inside the room shall be properly supported with MS hanger/tie rod .Refer tender specification for detail description. | item28 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
3.02 | 6.4 mm O.D (wall Thickness-1.0 mm) (insulation : 19 mm) | item29 | 140 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
3.03 | 9.5 mm O.D (wall Thickness-1.0 mm) (insulation : 19 mm) | item30 | 180 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.04 | 12.7 mm O.D (wall Thickness-1.0 mm) (insulation : 19 mm) | item31 | 155 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3.05 | 15.9 mm O.D (wall Thickness-1.0 mm) (insulation : 19 mm) | item32 | 200 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
3.06 | 19.1 mm O.D (wall Thickness-1.0 mm) (insulation : 19 mm) | item33 | 90 | Rmt | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3.07 | 22.2 mm O.D (wall Thickness-1.0 mm) (insulation : 19 mm) | item34 | 80 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
3.08 | 25.4 mm O.D (wall Thickness-1.0 mm) (insulation : 19 mm) | item35 | 40 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
3.09 | 28.6 mm O.D (wall Thickness-1.0 mm) (insulation : 19 mm) | item36 | 40 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
3.1 | 31.8 mm O.D (wall Thickness-1.0 mm) (insulation : 19 mm) | item37 | 60 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
3.11 | 34.9 mm O.D (wall Thickness-1.0 mm) (insulation : 19 mm) | item38 | 40 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
3.12 | 38.1 mm O.D (wall Thickness-1.0 mm) (insulation : 19 mm) | item39 | 80 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
3.13 | 41.3 mm O.D (wall Thickness-1.0 mm) (insulation : 19 mm) | item40 | 80 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
4 | Y-JOINTS & HEADERS | item41 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4.01 | Supply, installation, testing & commissioning of following imported OEM fittings to be provided in Supply & return refrigerant pipe line. Material of construction for fittings shall be similar to refrigerant piping. | item42 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
4.02 | Y- joints for IDU - IDU refrigerant piping | item43 | 42 | Set | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
4.03 | Y- joints for ODU - ODU refrigerant piping | item44 | 4 | Set | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
5 | Top-up additional Refrigerant R-410a charging | item45 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
5.01 | Supply, charging, and commissioing of additional R-410a (Du-pont/Honeywell) Refrigerant Gas charging on VRF system complete as required. | item46 | 120 | Kg | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
6 | MS ODU STAND | item47 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
6.01 | Structural steel work riveted, bolted or welded in built up sections, trusses and framed work, including cutting, hoisting, fixing in position and applying a priming coat of approved steel primer all complete. | item48 | 350 | Kg | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
7 | CABLE TRAY FOR REFRIGERANT PIPING | item49 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
7.01 | Supplying and installing of following size of perforated hot dip galvanized G.I cable tray with perforations not more than 17.5%, in convenient sections, joined with connectors, suspended from ceiling with G.I suspenders including bolts and nuts, etc. for carrying refrigerant pipe in outdoor application as required. | item50 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
7.02 | 450 mm width x 62.5 mm depth x 2 mm thickness | item51 | 200 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
7.03 | 225mm width x 50 mm depth x 1.6 mm thickness | item52 | 150 | Rmt | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
8 | CONDENSATE DRAIN UPVC PIPE | item53 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
8.01 | Supply, installation, testing and commissioning of uPVC Pipe, complete with fittings, supports,U trap arrangement,Clean Plug and accessories for IDUs as per specifications, drawings. | item54 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
8.02 | 32 mm dia (with 6mm Nitrile) | item55 | 150 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
8.03 | 40 mm dia (with 6mm Nitrile) | item56 | 200 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
9 | CHAPTER 2: AIR DISTRIBUTION SYSTEM | item57 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
9.01 | GSS DUCT (Factory Fabricated Duct) | item58 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
9.02 | Supply, installation,balancing and commissioning of factory fabricated GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers , supports etc. as per approved drawings and specifications of following sheet thickness complete as required . Refer tender specification for detail description. | item59 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
9.03 | 24 G (0.63 mm) | item60 | 530 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
9.04 | 22 G (0.80 mm) | item61 | 50 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
9.05 | GSS DUCT (Site Fabricated Duct) | item62 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
9.06 | Supply, installation,balancing and commissioning of fabricated at site GSS sheet metal rectangular/round ducting complete with neoprene rubber gaskets, elbows, splitter dampers, vanes, hangers , supports etc. as per approved drawings and specifications of following sheet thickness complete as required . Refer tender specification for detail description. | item63 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
9.07 | 24 G (0.63 mm) | item64 | 100 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
9.08 | 22 G (0.80 mm) | item65 | 20 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10 | Supply Air Grilles | item66 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
10.01 | Supplying & fixing of powder coated extruded aluminium Supply Air Grilles with Aluminium volume control dampers of various sizes and as per specifications and approved drawings and schedules. | item67 | 15 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
10.02 | Return Air Grilles | item68 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
10.03 | Supplying & fixing of powder coated extruded aluminium Return Air Grilles with louvers but without volume control dampers of various sizes and as per specifications and approved drawings and schedules. | item69 | 45 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
10.04 | Volume Control Damper | item70 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
10.05 | Supply, installation, testing and commissioning of GI volume control duct damper complete with neoprene rubber gaskets, nuts, bolts, screws linkages, flanges etc, as per specifications. | item71 | 4 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
10.06 | Motorised Volume Control Damper | item72 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
10.07 | Supply, installation, testing and commissioning of motorised(ON/OFF Type) duct mounted G.I volume control damper with enthalpy sensor and necessary control wiring (minimum 1.5 sqmm ) for integeration within IDU room. The unit shall provided as shown in the drawings. The unit shall be capable to communicate with BMS system. | item73 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
10.08 | Damper | item74 | 2 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
10.09 | Actuator | item75 | 4 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11 | Fresh Air Louvers | item76 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
11.01 | Supplying, installation, testing and commissioning of AL. construction fresh air louvers with min. 50 % free area , and painted in baked enamel shade with metallic frame work complete as per specification approved drawings and schedules. Louvers need to be suitable in order avoid rain water entry in to spaces @ 15 degree deflection with bird screen complete as per specification approved drawings and schedules. | item77 | 2 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
11.02 | flexible duct | item78 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
11.03 | Supply, installation, testing & commissioning of thermal insulated flexible duct of following sizes duly supported at regular interval as per site requirement etc. complete as required as per specifications. | item79 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
11.04 | Thermal insulated flexible duct (200 mm dia) | item80 | 45 | Rmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
12 | CHAPTER 3: INSULATION & ACOUSTIC | item81 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
12.01 | DUCT INSULATION | item82 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
12.02 | Supply,Installation,Testing and commissioning of Thermal insulation material for Duct insulation.It shall be anti-microbial XLPE type closed cell cross linked polyethylene foam with aluminium foil. Thermal conductivity of the insulation material shall not exceed 0.032 W/moK at an average temperature of 25oC. Density of the material shall be 25-30 Kg/m3. The product shall have temperature range of –40 oC to 105oC. The insulation material shall be fire rated for Class 0 for surface spread of flame test. Water vapour permeability shall not exceed 0.15ng/Pa.Sec.m. Thermal conductivity of the material shall not be affected by ageing, as per DIN 52616. The material must be tested for ageing effect in an accredited laboratory for a minimum period of five years to satisfy the ageing criteria. The smoke density of the material shall not exceed 1. There shall be no toxicity in the emitted smoke, both under flaming and non-flaming conditions. The quoted price shall include adhesive and accessories required to fix the insulation inside the duct. | item83 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
12.03 | 9 mm on supply/Return duct | item84 | 50 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
12.04 | 13 mm on supply/Return duct | item85 | 700 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
13 | DUCT ACOUSTIC LINING | item86 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
13.01 | Supply and fixing of acoustic lining of supply air duct and plenum with 25 mm thick resin bonded glass wool having density of 32 kg/m³, with 25 mm X 25 mm GI section of 1.25 mm thick, at 600 mm centre to centre covered with Reinforced Plastic tissue paper and 0.5 mm thick perforated aluminum sheet fixed to inside surface of ducts with cadmium plated nuts, bolts, stick pins, CPRX compound etc. complete as required and as per specifications. | item87 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
13.02 | Acoustic lining of supply air duct and plenum with 25 mm thick resin bonded glass wool having density of 32 kg/m³ | item88 | 200 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
14 | UNDERDECK INSULATION (for Exposed Roofs) | item89 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
14.01 | Supply,Installation,Testing and commissioning of Thermal insulation material for Underdeck insulation.It shall be chemical bonded anti-microbial closed cell cross linked polyethylene foam (XLPE) .Thermal conductivity of the insulation material shall not exceed 0.032 W/moK at an average temperature of 25oC. Density of the material shall be 25-30 Kg/m3. The product shall have temperature range of –40 oC to 105oC. The insulation material shall be fire rated for Class 0 as per BS 476 Part 7, 1987 for surface spread of flame test. Water vapour permeability as per DIN 52615 shall not exceed 0.15ng/Pa.Sec.m. | item90 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
14.02 | Thermal conductivity of the material shall not be affected by ageing, as per DIN 52616. The material must be tested for ageing effect in an accredited laboratory for a minimum period of five years to satisfy the ageing criteria. | item91 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
14.03 | The smoke density of the material as per AS-1530.3 shall not exceed 1. There shall be no toxicity in the emitted smoke, both under flaming and non-flaming conditions, as per AITM 3.000 (1993). The quoted price shall include adhesive and accessories required to fix the insulation inside the duct. It shall also be supported with wire mesh in addition to the adhesive. | item92 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
14.04 | 25 mm XLPE Insulation | item93 | 540 | Sqmt | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
15 | DOUBLE LAYER CANVAS CONNECTION | item94 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
15.01 | Supply,Installation,testing and commissioning of double Layer canvas connection fire retardant cloth for the end connection of IDUs and Ventilation fan to reduce the vibration.It shall be fire rated for atleast 2 hrs.Refer tender specification for detail description | item95 | 32 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16 | CHAPTER 4: VENTILATION SYSTEM | item96 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
16.01 | FIRE RATED TUBE AXIAL FLOW FANS FOR PLANT ROOM VENTILATION | item97 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
16.02 | Supply, installation, testing and commissioning of Fire Rated Tube Axial flow fans complete with tube casing, impeller, bird screen, gravity louvers, necessary nut bolts, Necessary transition piece and canvas connection for proper Installing, silencers on inlet and outlet and directly coupled TEFC Sq.cage, IE-2 efficiency induction motor mounted on vibration isolators suitable for 415V±10%, 50 Hz. 3 phase electric supply complete as per the technical specifications enclosed. The fans should be AMCA certified for air performance & sound ratings. The fan should be rated for a minimum of 250 Deg C for a minimum of 2 Hrs. Application.The fan shall be complete in all respect and should match the specification ,Drawings and Schedule.The quoted price shall consist of mounting arrangemnt along with spring isolator for fan.The unit shall be capacble to communicate with BMS system. | item98 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
16.03 | The speed of the motor shall be less than 1450 RPM and the impeller speed shall be less than 1000 RPM and capacities based on minimum static pressure to suit the system. | item99 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
16.04 | Note:Noise level shall be 80 db(A) @ 3 meter distance from fan at room condition. | item100 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
16.05 | 3000 CFM ,Total static pressure of 20 MM WG (Smoke Exhaust Fan) | item101 | 4 | Nos. | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
17 | PROPELLER FANS | item102 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
17.01 | Supply , installation , testing and commissioning of propeller type fan with Aluminium/Plastic blade and complete with induction Motor suitable for operation with 230 V single phase 50 Hz with suitable frame etc. as per IS:2312-1967 with gravity dampers for exhaust complete as per specifications and drawings. Noise level should not exceed 45dB(A) @3m.The fan shall be complete in all respect and should match the specification ,Drawings and Schedule.system. | item103 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
17.02 | 100 CFM | item104 | 8 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
17.03 | 150 CFM | item105 | 8 | Nos. | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
18 | CHAPTER 5: ELECTRICAL | item106 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
18.01 | HVAC PANEL Incomer : MCCB 415V, 50Hz, 400A, 4P, 25kA for 1 sec rated thermal magnetic based MCCB with inbuilt LSIG protection - 1 Nos. Metering (1 No.) Multifunction meter with inbuilt selector switch for measurement of current, voltage, power factor, KVA, kVAh, KVArh, KVAR, frequency, ,KWHr (both line and phase) complete as per specifications Indication lamps LED type phase indication lamps suitable for 230V,50Hz AC (red, yellow, blue) - 1 Set. LED type Indication lamps for breaker, suitable for 230V,50Hz AC supply (on, off, trip) - 1 set CTs: 415V ,400/5A, 15VA, CL-1 current transformer for metering | item107 | 1 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
18.02 | Busbar : | item108 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
18.03 | Busbar (1 Set - 4P + E) Busbar made up of electrolytic grade high conductivity aluminium in rectangular cross section and suitable for 415V, FP, 50 Hz, 400 A, 25 kA for 1 sec of required length and cross sectional area. | item109 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
18.04 | Outgoing : | item110 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
18.05 | MCB 12 Nos. 415V, 50Hz, 63A, 4P, 10 kA MCB. 5Nos. 415V, 50Hz, 40A, 4P, 10 kA MCB. | item111 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
18.06 | EARTHING | item112 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
18.07 | Supply & Laying of following Tinned copper earth wire/earth strip, GI earth wire/strip fixed on wall/side of trench/slab /column /beam/ shaft, connection to panel/DBs/SFU's etc. with 5mm thick G.I./Cu. Spacers & 2mm thick G.I./ Cu. Saddle including connection/termination with suitable GI/Cu. thimble & nut bolts etc as required to do the job in all respect in accordance with laid specification, drawing or upto the satisfaction of engineer in charge. | item113 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
18.08 | 25x5 mm G.I. Strip | item114 | 80 | Metre | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19 | LT CABLE AND TERMINATION | item115 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
19.01 | Supplying, unloading, storing , laying, testing and commissioning of following sizes of 1.1 kV grade XLPE insulated, FRLS (Heavy duty) Copper conductor armoured cables suitable for working voltage upto and including 1100 Volts, laid and tied on existing overhead cable trays; or buried underground or laid and tied over MS supports in masonry trenches including providing MS supports and clamps for fixing to supports in an approved manner, providing fire retardant sealant where required complete as required and as per specifications. Circuit identification tag should be attached with the concerned cable alongwith the test report of following sizes of cable to be submitted by the contractor at the time of delivery of material at site. (Cable length may increse as per existing panel location). | item116 | [52 empty] | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
19.02 | 4C X 16 Sqmm 2XWY. | item117 | 120 | Metre | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
19.03 | 4C X 10 Sqmm 2XWY. | item118 | 40 | Metre | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
19.04 | Supplying and making end termination with single compression brass gland and lugs for following size of XPLE insulated and PVC sheathed /XLPE aluminum or copper conductor cable of 1.1 KV grade of the following sizes as required. The cost shall include the cost of crimping and all tools and accessories required to complete the job in full respect. Note : Al lugs shall be used for Al cable and cu lugs shall be used for copper cable. | item119 | [52 empty] | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
19.05 | 4C X 16 Sqmm 2XWY. | item120 | 16 | Each | 100 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
19.06 | 4C X 10 Sqmm 2XWY. | item121 | 4 | Each | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
20 | CHAPTER 6: Comprehensive Annual Maintenance of complete VRF System alongwith controller & its software | item122 | [52 empty] | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
20.01 | Annual comprehensive maintenance contract of capacity as above annexure of complete VRF system which cover's all spares, controlller, hardware, software and consumables requirement to run the VRF system of capacity 176 HP after expiring of 1 year (12 Months) defect liability period. | item123 | [52 empty] | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.02 | For 1st year (0-12 Months) | item124 | 12 | Mth | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
20.03 | For 2nd year (12-24 Months) | item125 | 12 | Mth | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 2 | Construction of chamber for 100mm sluices valve | item3 | 10 | Nos
20.04 | For 3rd year (24-36 Months) | item126 | 12 | Mth | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 3 | Supplying, Conveying and fixing spls. Including ea | item4 | 10 | Nos
20.05 | For 4th year (36-48 Months) | item127 | 12 | Mth | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.01 | Supplying, Conveying and fixing spls. Including eart | item1 | 123.223 | Nos
20.06 | For 5th year (48-60 Months) | item128 | 12 | Mth | 10 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 0 | 0 | INR Zero Only | 1.02 | Construction of chamber for 100mm sluice plates | item2 | 213 | Nos
Total in Figures | [51 empty] | 0 | 0 | INR Zero Only | 4 | Construction of chamber for 100mm sluice plates | item5 | 10 | Nos
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | Zero Only
Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information