## BoQ1 (hidden)
Percentage BoQ
BoQ_Ver3.1 | Percentage | Normal | INR Only | INR
Select, At Par, Excess (+), Less (-) |  | IOCL
Tender Inviting Authority: DOIP, IIT Kanpur
Name of Work: Repairing of damaged HT cables running between different substations and other associated works at IIT Kanpur
NIT No: Electrical/12/01/2024-1
Name of the Bidder/ Bidding Firm / Company :
PRICE SCHEDULE (This BOQ template must not be modified/replaced by the bidder and the same should be uploaded after filling the relevant columns, else the bidder is liable to be rejected for this tender. Bidders are allowed to enter the Bidder Name and Values only )
NUMBER # | TEXT # | TEXT # | NUMBER # | TEXT # | NUMBER | NUMBER | TEXT | TEXT # | NUMBER # | TEXT# | TEXT # | NUMBER # | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER | NUMBER | TEXT | TEXT | NUMBER | NUMBER | NUMBER # | NUMBER # | TEXT | TEXT | NUMBER # | NUMBER # | DATE | NUMBER # | NUMBER # | TEXT #
Sl. No. | Item Description | Item Code / Make | Quantity | Units | Estimated Rate in Rs. P |  |  | Addition / Deduction | Addition / Deduction Values | Currency Convertion against each Item | Quoted Currency in INR / Other Currency | BASIC RATE In Figures To be entered by the Bidder Rs. P | Excise Duty | VAT | Freight Charges ( Unloading & Stacking) | Any Other Taxes/Duties/Levies |  |  | Other Taxes 2 | IIIrd Party i.e DGS&D / RITES etc Inspection Charges @0.34%+Service Tax | Less for Cenvat Credit,if any respect of Supplies Under full Excise Duty Category | [30 empty] | TOTAL AMOUNT in Rs. P | TOTAL AMOUNT With Taxes | TOTAL AMOUNT In Words
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 7 | 54 | 8
1 | supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required : | item no.1 | [52 empty] | 1.01 | Supply installation testing and commissioning of cubical type LT panel-01 (IEC 61439 ) suitable for 4000Amp 415V, 3 phase, 4 wire 50 Hz AC supply system fabricated in compartmentalized (preferable) design from CRCA sheet steel of 2mm thick for frame work and covers. 3mm thick for gland plated i/c cleaning & finishing complete with 7 tank process for powder coating in approved shade, having suitable capacity extensible type FP Aluminium alloy Bus bars of high conductivity. DMC.SMC bus bar supports, with short circuit withstand capacity of 50 KA for 1 sec. bottom base channel of MS section not less than 100mm x 50mm x 5mm thick, fabrication shall be done in transportable sections, entire panel shall have a common earth bar of suitable size at the rear with 2 Nos earth solid connections from main bus bar to switch gears with required 1.5 sqmm zero halogen fire retardant low smoke insulated copper conductor s/c cable, cable alleys, cable gland plate in two half. | item no.1 | 1 | supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required : | item no.1
2 | 120-240sq. mm | item no.2 | 1 | Each | 14247.26 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 14247 | 14247 | INR Fourteen Thousand Two Hundred & Forty Seven Only | 1.02 | The panel shall be equipped with relays, timers set of CT's for metering & protection and energy analyser/meter (on all incomer and outgoing feeders) to indicate current phase, line voltage, frequency, power factor, KWH, KVARH. Provision of over load, short circuit, restricted earth fault, under frequency control cabling and interlocking, suitable cable termination chambers/ bus bars extension and providing indicating lamps of phases for all feeders complete with foundation as per drawing and specifications amended up to date complete. and attached specification. | item no.2 | 2 | 120-240sq. mm | item no.2 | 1 | Each
3 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required : | [56 empty] | 3 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminium conductor cable of 11 KV grade as required :
4 | 70-120 sq. mm |  | 1 | Each | 33391.49 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 33391 | 33391 | INR Thirty Three Thousand Three Hundred & Ninety One Only |  |  |  | 4 | 70-120 sq. mm |  | 1 | Each
5 | 120-240 sq. mm |  | 4 | Each | 36731.26 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 146925 | 146925 | INR One Lakh Forty Six Thousand Nine Hundred & Twenty Five Only |  |  |  | 5 | 120-240 sq. mm |  | 4 | Each
6 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level : | [56 empty] | 6 | Providing and laying in position cement concrete of specified grade excluding the cost of centering and shuttering - All work up to plinth level :
7 | 1:2:4 (1 Cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 40 mm nominal size derived from natural sources) |  | 1 | Cum | 6336.65 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 6337 | 6337 | INR Six Thousand Three Hundred & Thirty Seven Only |  |  |  | 7 | 1:2:4 (1 Cement : 2 coarse sand (zone-III) derived from natural sources : 4 graded stone aggregate 40 mm nominal size derived from natural sources) |  | 1 | Cum
8 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge. | [56 empty] | 8 | Demolishing brick work manually/ by mechanical means including stacking of serviceable material and disposal of unserviceable material within 50 metres lead as per direction of Engineer-in-charge.
9 | In mud mortar | item no.3 | 2 | Cum | 509.56 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 1019 | 1019 | INR One Thousand &Nineteen Only | 1.03 | Incoming | item no.3 | 9 | In mud mortar | item no.3 | 2 | Cum
10 | Supplying and laying of one No. PVC insulated/PVC sheathed 6.6 KV(UE) 11kV(E) grade XLPE HT power cables size 3x185sqmm (heavy duty) aluminium conductor, steel armoured cable as per , IS:7098 (Part-II/2011) as reqd. | item no.4 | [52 empty] | 1.04 | 2 No's 4000A, FP, EDO,50KA, ACB with microprocessor release (O/L, S/C & E/F protention) saftey shutter,SCM, CC, 4NO+4NC Aux. Contacts, interlock, shunt Trip contact T&C. etc. suitable to connect with the bus duct and through cables. ABB-Emax2/ Schneider MTZ/Siemens 3VA | item no.4 | 10 | Supplying and laying of one No. PVC insulated/PVC sheathed 6.6 KV(UE) 11kV(E) grade XLPE HT power cables size 3x185sqmm (heavy duty) aluminium conductor, steel armoured cable as per , IS:7098 (Part-II/2011) as reqd. | item no.4
11 | in girect ground | item no.5 | 70 | Mtr | 1856.2 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 129934 | 129934 | INR One Lakh Twenty Nine Thousand Nine Hundred & Thirty Four Only | 1.05 | breaker control switch TNC, Digital voltmeter/Ammeter Cl-1.0 with selector switch, Electronic KWH meter Cl-1.0, CT-4000/5A, Cl1.0, 15KVA cast rasin for metering, protection CTs 4000/5A, Cl-5P10, 15VA cast rasin IDMT relay , Trip circuit supervision relay , Phase indicating Lamp LED Type"Red, Tellow, Blue" Auto / Amnual selector switch Auxiliary contactors with 2NO+2NC , 2A SP MCB 10KA for cont. CKT. | item no.5 | 11 | in girect ground | item no.5 | 70 | Mtr
12 | Dismentling and refixing brass compression type gland 95 sq.mm up to 185 sq. mm. cable | item no.6 | 6 | Each | 375.27 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 2252 | 2252 | INR Two Thousand Two Hundred & Fifty Two Only | 1.06 | Both Incomer shall have class-b SPD of DEHN make. With 50KA 40A MPCB Protection. | item no.6 | 12 | Dismentling and refixing brass compression type gland 95 sq.mm up to 185 sq. mm. cable | item no.6 | 6 | Each
13 | Digging cable trench, lifting brick and cable for locating fault and relaying the cable I/c refilling the trench for extra sand if required shall be including in the item of size 120 sq.mm upto 185 sq.mm. as reqd. | item no.7 | 50 | Mtr | 236.74 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 11837 | 11837 | INR Eleven Thousand Eight Hundred & Thirty Seven Only | 1.07 | Bus bar: 1 No.4000 A, 50HZ, FP, Aliminium Bus Bar | item no.7 | 13 | Digging cable trench, lifting brick and cable for locating fault and relaying the cable I/c refilling the trench for extra sand if required shall be including in the item of size 120 sq.mm upto 185 sq.mm. as reqd. | item no.7 | 50 | Mtr
14 | Locating fault of by using fault locating machine for 11KV cable ( HT cable ) in the cable lines meggaring etc and rectifying removing & restoring the same and making good the damages 11KV cable etc as directed by the Engineer Incharge. | item no.8 | 4 | Nos. | 13493.2 |  |  | Excess(+) | 1 | Full Conversion | INR | [40 empty] | 53973 | 53973 | INR Fifty Three Thousand Nine Hundred & Seventy Three Only | 1.08 | OutGoing: | item no.8 | 14 | Locating fault of by using fault locating machine for 11KV cable ( HT cable ) in the cable lines meggaring etc and rectifying removing & restoring the same and making good the damages 11KV cable etc as directed by the Engineer Incharge. | item no.8 | 4 | Nos.
Total in Figures | [51 empty] | 399915 | 199015 | Three Lakh Ninety Nine Thousand Nine Hundred & Fifteen Only |  |  |  | Total in Figures |  | 29911889
Quoted Rate in Figures |  |  |  | Select | [47 empty] | 0 | 0 | INR Zero Only |  |  |  | Quoted Rate in Figures |  | Excess (+)
Quoted Rate in Words |  | INR Zero Only | [55 empty] | Quoted Rate in Words |  | INR Zero Only

## Macros
Please Enable Macros to View BoQ information